[IMAGE: WakeCap Logo - Company letterhead placeholder]

POWER SOLUTIONS

Operations Selection Guide

Site Assessment & Solution Selection for Field Deployment

[IMAGE: Decision flowchart graphic or product lineup comparison image]

Document: WC-PS-OSG-v1.1     |     February 2026

INTERNAL USE - OPERATIONS DEPARTMENT

Target: Project Engineers | Site Engineers | Operations Managers

# TABLE OF CONTENTS

1. Quick Selection Guide ......................................................... 3

2. Load Calculation Fundamentals ........................................... 4

3. Product Specifications Comparison ...................................... 6

4. Site Assessment Checklist .................................................. 8

5. Environmental Considerations ............................................. 10

6. Installation Requirements ................................................... 11

7. Solution Selection Decision Tree ......................................... 13

8. Common Deployment Scenarios ........................................... 14

# 1. Quick Selection Guide

Use this section for rapid solution selection based on your equipment load requirements.

## 1.1 Selection by Load

Match your total system power consumption to the appropriate Power Solution:

| Total System Load | Recommended Solution | Typical Equipment | Backup Time* |
| --- | --- | --- | --- |
| ≤ 8W | WakeCap Power 30 (WP-30) | WakeCap Gateway only | 48+ hours |
| 9W - 15W | WakeCap Power 60 (WP-60) | Single bullet camera, small sensor | 48+ hours |
| 16W - 100W | WakeCap Power 400 (WP-400T) | PTZ camera, multiple bullets, gateway + cameras | 48+ hours |
| 101W - 350W | WakeCap Power 900 (WP-900T) | Multiple PTZ cameras, comm equipment | 48+ hours |

* Backup time assumes zero solar input (worst case). Actual runtime varies with solar conditions.

⚡ IMPORTANT Always calculate TOTAL SYSTEM POWER, not just device power. System power includes the device, PoE injectors, routers, voltage converters, and all auxiliary equipment.

## 1.2 Equipment Power Reference

Standard power consumption for common equipment:

| Equipment Type | Device Power | System Power* | Notes |
| --- | --- | --- | --- |
| WakeCap Gateway | ~5W | ~8W | Includes power conversion losses |
| Bullet Camera (standard) | 15W | 35W | Includes PoE injector, router |
| PTZ Camera (Type 1) | 42W | 70W | Mid-range PTZ with PoE |
| PTZ Camera (Type 2) | 62W | 90W | High-end PTZ with heater |
| Network Router/Switch | 5-15W | — | Add to system total |
| PoE Injector | 3-8W | — | Conversion losses |

* System Power = Device + PoE + Router + Conversion Losses. Always use System Power for selection.

# 2. Load Calculation Fundamentals

Proper load calculation is essential for selecting the correct power solution. Follow this systematic approach.

## 2.1 Calculation Order

Power system sizing follows this sequence:

1. LOAD - Calculate total continuous power consumption

2. BATTERY - Size battery bank for required backup duration

3. SOLAR - Size solar array to recharge battery daily

4. MPPT - Select controller to handle solar current

5. AUXILIARY - Add protection, cabling, mounting

## 2.2 Standard Design Parameters

All WakeCap Power Solutions are designed using these parameters:

| Parameter | Symbol | Value | Description |
| --- | --- | --- | --- |
| Backup Time | T | 48 hours | Required autonomy without solar input |
| Depth of Discharge | DoD | 70% | Usable battery capacity |
| System Efficiency | η_sys | 90% | Wiring and general losses |
| Converter Efficiency | η_conv | 80% | DC-DC conversion losses |
| Solar Derating | η_solar | 75% | Dust, misalignment, temperature |
| MPPT Efficiency | η_mppt | 95% | Charge controller efficiency |
| Peak Sun Hours | PSH | 6.5 hours | Saudi Arabia average |

## 2.3 Battery Capacity Formula

Required battery capacity (Ah) for a given load:

Battery (Ah) = (T × Load) / (DoD × η_sys × η_conv × V)

Where: T = 48h, DoD = 0.70, η_sys = 0.90, η_conv = 0.80, V = System Voltage

## 2.4 Example Calculation

Calculate the solution for a single PTZ Camera (Type 1) system:

- System Load: 70W (42W camera + PoE + router)

- System Voltage: 12V

- Required Battery = (48 × 70) / (0.70 × 0.90 × 0.80 × 12)

- Required Battery = 3360 / 6.048 = 556 Ah

ℹ NOTE A 70W load requires approximately 556Ah battery capacity. The WP-400T (400Ah) is insufficient; select WP-900T (900Ah @ 24V = equivalent to ~450Ah usable at 12V reference, but provides 24V system) for margin. Alternatively, reduce load or accept shorter backup time.

## 2.5 Load Capacity Summary

Maximum continuous loads per solution (for 48-hour backup):

| Solution | Battery Capacity | Max Load (48h backup) | Max Load (24h backup) |
| --- | --- | --- | --- |
| WP-30 | 30Ah / 384Wh | ~8W | ~16W |
| WP-60 | 60Ah / 768Wh | ~15W | ~30W |
| WP-400T | 400Ah / 4,800Wh | ~100W | ~200W |
| WP-900T | 900Ah @ 24V / 21,600Wh | ~350W | ~700W |

# 3. Product Specifications Comparison

## 3.1 Power System Specifications

| Specification | WP-30 | WP-60 | WP-400T | WP-900T |
| --- | --- | --- | --- | --- |
| System Voltage | 12V DC | 12V DC | 12V DC | 24V DC |
| Battery Capacity | 30Ah | 60Ah | 400Ah (2×200) | 900Ah (6×150) |
| Battery Energy | 384Wh | 768Wh | 4,800Wh | 21,600Wh |
| Battery Type | LiFePO4 | LiFePO4 | GEL Lead Acid | HT Lead Acid |
| Solar Power | 80W | 100W | 450W | 1,305W |
| Solar Panels | 2 × 40W | 2 × 50W | 3 × 150W | 3 × 435W |
| MPPT Controller | Integrated | 10A | 30A | 60A EPEVER |
| MPPT Efficiency | >95% | 96.5% | 95% | 98% |
| Output Voltage | 12V ±0.5V | 10.5-12.6V | 12V DC | 24V DC |
| Max Output Current | 3A | 10A | <30A (25A typical) | <60A (55A typical) |

## 3.2 Physical Specifications

| Specification | WP-30 | WP-60 | WP-400T | WP-900T |
| --- | --- | --- | --- | --- |
| Total Weight | ~6 kg | 23 kg | 525 kg | 1,300 kg |
| Form Factor | Pole/Wall Mount | Bracket Mount | Trailer | Trailer |
| Mast Height | N/A | N/A | 6.5m (pneumatic) | 9m (manual) |
| Transport Size (mm) | 780×530×200 | 940×780×240 | 2000×1400×2300 | 2320×1495×2350 |
| Deployed Size (mm) | 780×530×varies | 940×780×varies | 2000×2250×6500 | 2320×1495×2350 (+ mast) |
| Trailer Type | N/A | N/A | Single axle | Single axle |
| Tow Hitch | N/A | N/A | Ball hitch | 50mm ball hitch |
| Tire Size | N/A | N/A | 165/70R13 | 15" |

## 3.3 Environmental Ratings

| Specification | WP-30 | WP-60 | WP-400T | WP-900T |
| --- | --- | --- | --- | --- |
| IP Rating | IP66 | IP66 | IP65 | IP65 |
| Operating Temp | -20°C to +50°C | -30°C to +85°C | -20°C to +80°C | -20°C to +85°C |
| Charge Temp (Low) | -10°C | -30°C | [TBD] | [TBD] |
| Discharge Temp (Low) | -20°C | -30°C | [TBD] | [TBD] |
| Wind Rating (Panel) | 2400Pa | 60m/s (200kg/m²) | 100 km/h | 100 km/h |
| Snow Load | 5400Pa | [TBD] | [TBD] | [TBD] |

💡 TIP LiFePO4 batteries (WP-30, WP-60) offer better cold weather performance and longer cycle life. GEL/Lead Acid batteries (WP-400T, WP-900T) are more cost-effective for high-capacity applications but require more frequent replacement.

# 4. Site Assessment Checklist

Complete this assessment before selecting and deploying a Power Solution.

## 4.1 Load Requirements

□ List all equipment to be powered:

- Equipment 1: _____________ Power: _____ W

- Equipment 2: _____________ Power: _____ W

- Equipment 3: _____________ Power: _____ W

- PoE Injectors / Converters: _____ W

- Network Equipment: _____ W

□ TOTAL SYSTEM LOAD: _________ W

□ Required backup time without solar: _________ hours (standard: 48h)

## 4.2 Site Access

□ Access road available for:

- Light vehicle (WP-30, WP-60): □ Yes □ No

- Pickup truck with trailer (WP-400T): □ Yes □ No

- Heavy truck with trailer (WP-900T): □ Yes □ No

□ Site accessible during deployment period: □ Yes □ No

□ Crane or lifting equipment available (if needed): □ Yes □ No

## 4.3 Ground Conditions

□ Ground type: □ Compacted soil □ Sand □ Gravel □ Concrete □ Other: _______

□ Ground is level (within 5°): □ Yes □ No

□ Ground can support trailer weight: □ Yes □ No □ N/A

□ Anchor points available (for trailers): □ Yes □ No □ N/A

## 4.4 Mounting Structure (WP-30, WP-60 only)

□ Existing pole available: □ Yes □ No

□ Pole diameter: _________ mm (WP-30 clamps fit Ø150mm)

□ Pole structural capacity verified: □ Yes □ No

□ Wall mounting possible: □ Yes □ No

## 4.5 Solar Exposure

□ Clear southern sky exposure: □ Yes □ Partial □ No

□ Shading from structures/equipment: □ None □ Morning □ Afternoon □ Full day

□ Estimated Peak Sun Hours: _________ hours/day (Saudi average: 6.5h)

□ Seasonal variation considered: □ Yes □ No

# 5. Environmental Considerations

Saudi Arabia deployment environments require special attention to these factors.

## 5.1 Desert Environment

- High ambient temperatures (up to 50°C+)

- Solar panel derating at high temperatures (expect 10-15% reduction)

- Battery capacity reduction at extreme temperatures

- Dust accumulation on solar panels - plan monthly cleaning

- Sand/dust ingress - verify IP rating adequate for location

ℹ NOTE At temperatures above 45°C, expect reduced charging efficiency and shorter battery runtime. LiFePO4 batteries (WP-30, WP-60) handle heat better than Lead Acid (WP-400T, WP-900T). Consider shading the battery enclosure if possible.

## 5.2 Coastal/Humid Environment

- Salt air accelerates corrosion on exposed metal

- Higher humidity reduces solar panel efficiency slightly

- Verify all connections are sealed and protected

- More frequent maintenance inspections recommended

- Consider additional corrosion protection for trailer frames

## 5.3 Wind Considerations

Maximum wind ratings by product:

- WP-30/WP-60: Solar panels rated for 60 m/s (216 km/h)

- WP-400T/WP-900T: Mast should be lowered in high winds

- WP-900T: System rated for 100 km/h wind speed

⚡ IMPORTANT Always lower trailer masts before wind speeds exceed 50 km/h. Extended masts act as significant wind loads and can cause trailer instability or structural damage.

## 5.4 Security Considerations

- Site fencing recommended for all trailer deployments

- Wheel locks and hitch locks for theft deterrence

- Consider GPS tracking for high-value trailer units

- Remote monitoring via cellular (if available) for intrusion alerts

# 6. Installation Requirements

## 6.1 Personnel Requirements

| Solution | Min. Personnel | Skill Level | Special Equipment |
| --- | --- | --- | --- |
| WP-30 | 1 technician | Basic electrical | Ladder, hand tools |
| WP-60 | 1 technician | Basic electrical | Ladder, hand tools, drill |
| WP-400T | 2 technicians | Electrical + mechanical | Tow vehicle, level, hand tools |
| WP-900T | 2-3 technicians | Electrical + mechanical | Heavy tow vehicle, level, hand tools |

## 6.2 Installation Time Estimates

| Solution | Setup Time | Equipment Connection | Commissioning | Total |
| --- | --- | --- | --- | --- |
| WP-30 | 30 min | 15 min | 15 min | ~1 hour |
| WP-60 | 45 min | 15 min | 15 min | ~1.25 hours |
| WP-400T | 1.5 hours | 30 min | 30 min | ~2.5 hours |
| WP-900T | 2 hours | 45 min | 30 min | ~3.25 hours |

## 6.3 Pre-Installation Checklist

□ Site assessment completed (Section 4)

□ Equipment manifest verified against delivery

□ All components present and undamaged

□ Battery state of charge verified (>40% recommended)

□ Tools and PPE available

□ Weather conditions acceptable (no rain, wind < 30 km/h)

□ Communication with site supervisor confirmed

## 6.4 Solar Panel Orientation

For optimal energy harvest in Saudi Arabia:

- Panel orientation: SOUTH (0° azimuth)

- Tilt angle: 20-30° from horizontal (WP-60 adjustable 0-30°)

- Seasonal adjustment: 15° summer, 35° winter (if accessible)

- Avoid any shading, especially partial shading across cells

## 6.5 Trailer Setup Procedure (WP-400T, WP-900T)

1. Position trailer on level ground with southern sky exposure

2. Engage parking brake and chock wheels

3. Deploy outriggers and level trailer (WP-400T)

4. Disconnect from tow vehicle

5. Deploy and orient solar panels

6. Raise mast to desired height

7. Mount equipment to mast/camera box

8. Connect equipment cables

9. Verify system operation

# 7. Solution Selection Decision Tree

Follow this flowchart to select the appropriate Power Solution:

[IMAGE: Decision tree flowchart: Start → Calculate Load → Select by load range → Verify site access → Confirm selection]

## 7.1 Decision Steps

1. Calculate TOTAL SYSTEM LOAD (not device power alone)

2. Check load against solution capacity table (Section 1.1)

3. Verify site access for selected solution

4. Confirm environmental compatibility

5. If multiple solutions qualify, prefer smaller for cost savings

6. If borderline, select larger solution for margin

## 7.2 Quick Decision Matrix

| If your load is... | And site has... | Select... |
| --- | --- | --- |
| ≤8W (Gateway only) | Existing pole/wall | WP-30 |
| 9-15W (single camera) | Existing structure | WP-60 |
| 16-100W (PTZ or multi-camera) | Vehicle access + level ground | WP-400T |
| 101-350W (surveillance system) | Heavy vehicle access + space | WP-900T |
| >350W | Any | Multiple units or custom solution |

# 8. Common Deployment Scenarios

## 8.1 Scenario A: Remote Gateway

Situation: WakeCap Gateway for worker tracking at isolated site

- Equipment: WakeCap Gateway (~8W system)

- Solution: WP-30

- Mounting: Existing pole or temporary pole

- Installation: 1 technician, ~1 hour

## 8.2 Scenario B: Single Bullet Camera

Situation: Security camera monitoring equipment yard

- Equipment: Bullet camera + PoE + router (~35W system)

- Solution: WP-60 (15W continuous allows 24h backup at 35W)

- Alternative: WP-400T for full 48h backup

- Mounting: Bracket on structure or dedicated pole

- Installation: 1 technician, ~1.25 hours

## 8.3 Scenario C: Single PTZ Camera

Situation: PTZ surveillance camera at remote checkpoint

- Equipment: PTZ camera Type 1 (~70W system)

- Solution: WP-400T (100W capacity with margin)

- Mounting: Trailer mast (6.5m height)

- Installation: 2 technicians, ~2.5 hours

## 8.4 Scenario D: Multi-Camera Surveillance

Situation: Construction site perimeter monitoring

- Equipment: 2× PTZ cameras + 1× bullet + router (~200W system)

- Solution: WP-900T (350W capacity)

- Mounting: Trailer mast (9m height)

- Installation: 2-3 technicians, ~3.25 hours

- Note: Consider communication equipment power if cellular backhaul needed

## 8.5 Scenario E: High-Power PTZ System

Situation: High-end PTZ with heating element in harsh environment

- Equipment: PTZ Type 2 (~90W) + backup camera (~35W) = 125W system

- Solution: WP-900T

- Note: WP-400T insufficient for 48h backup at 125W

ℹ NOTE For some sites, deploying multiple smaller units may be more practical than one large unit. Example: Two WP-60 units for separate cameras vs. one WP-400T requires no trailer access but needs two mounting structures.

END OF DOCUMENT

WakeCap Power Solutions - Operations Selection Guide v1.1

For technical support: [TBD - Operations Support Contact]